## Slide 1: Industrial Electronics
Dr. Imtiaz Hussain
Assistant Professor
Mehran University of Engineering & Technology Jamshoro
email: imtiaz.hussain@faculty.muet.edu.pk
URL :http://imtiazhussainkalwar.weebly.com/
Lecture-5
Programmable Logic Controller
STEVTA -Training of Trainers Project

## Slide 2
Outline
Introduction to PLCs
Structure of PLC
  Central Processing Unit
  Input/output System
Programming Concepts

## Slide 3: Definition of PLC
Programmable Logic Controllers are solid state devices that can be programmed to performed sequential and discrete state operation on external equipment
They are designed to perform the logic functions previously accomplished by electromechanical relays, drum switches, mechanical and electronic timers and counters, standalone digital PID controllers etc.

## Slide 4: PLC’s Are...
Dissimilar to Microcontrollers:
  Intended for Industrial Applications
  I/O Designed to interface with Control Relays
  Emphasis on Maximum Reliability

## Slide 5: Advantages of PLC
1. Flexibility
    v Universal Controller - can replace various independent/ standalone controller.
  2. Implementing Changes and Correcting Errors
    v Do not have to rewiring relay panel.
    v Change program using keyboard.
  3. Large Quantity of Contact
    v Large number of' Soft Contact' available.
  4. Lower Cost
    v Advancement in technology and open architecture of PLC will reduce the market price.
  5. Pilot Running (Simulation Capability)
    v A program can be simulated or run without actual input connection.

## Slide 6: Advantages of PLC
Visual Observation.
  Can observe the opening and closing of contact switch on CRT .
  Operator message can be programmed for each possible malfunction.
Speed of Operation
  Depends on scan time -millisecond.
  Asynchronous operation.
Ladder or Boolean Programming Method.
  Easy for 'Electrician ,
Reliability
  In general -very reliable
Simplicity of Ordering Control Sys. Components
  One package with Relay, Timers, Control Block, etc.

## Slide 7: Advantages of PLC
Documentation
  Printout of ladder logic can be printed easily
Security
  Software lock on a program (Password)
Ease of Changes by Programming
  Ability to program and reprogram, loading and down loading

## Slide 8
8
Leading Brands Of PLC
AMERICAN 1. Allen Bradley
2. Gould Modicon
3. Texas Instruments
4. General Electric
5. Westinghouse
6. Cutter Hammer
7. Square D
EUROPEAN 1. Siemens
2. Klockner & Mouller
3. Festo
4. Telemechanique
JAPANESE 1. Toshiba
2. Omron
3. Fanuc
4. Mitsubishi

## Slide 9
9
Areas of Application
Manufacturing / Machining
Food / Beverage
Metals
Power
Mining
Petrochemical / Chemical

## Slide 10
10
PLC Size
1. SMALL - It covers units with up to 128 I/O’s and memories up to 2 Kbytes.
- These PLC’s are capable of providing simple to advance levels or machine controls.
MEDIUM - have up to 2048 I/O’s and memories up to 32 Kbytes.
3. LARGE - the most sophisticated units of the PLC family. They have up to 8192 I/O’s and memories up to 750 Kbytes.
- can control individual production processes or entire plant.

## Slide 11
11
Major Components of a Common PLC
PROCESSOR
POWER
SUPPLY
I M
N O
P D
U U
T L
E
O M
U O
T D
P U
U L
T E
PROGRAMMING DEVICE
From SENSORS
Pushbuttons,
contacts,
limit switches,
etc.
To
OUTPUT
Solenoids, contactors, alarms
etc.

## Slide 12
12
Major Components of a Common PLC
POWER SUPPLY
Provides the voltage needed to run the primary PLC components
I/O MODULES
Provides signal conversion and isolation between the internal logic- level signals inside the PLC and the field’s high level signal.

## Slide 13
13
Major Components of a Common PLC
PROCESSOR
Provides intelligence to command and govern the activities of the entire PLC systems.
PROGRAMMING DEVICE
used to enter the desired program that will determine the sequence of operation and control of process equipment or driven machine.

## Slide 14
14
Programming Device
    Types:
    Hand held unit with LED / LCD display
    Desktop type with a CRT display
    Compatible computer terminal

## Slide 15
15
I/O Module
The I/O interface section of a PLC connects it to external field devices.
The main purpose of the I/O interface is to condition the various signals received from or sent to the external input and output devices.
Input modules converts signals from discrete or analog input devices to logic levels acceptable to PLC’s processor.
Output modules converts signal from the processor to levels capable of driving the connected discrete or analog output devices.

## Slide 16
16
I/O Module
DC INPUT MODULE
OPTO-
ISOLATOR
IS NEEDED TO:
Prevent voltage transients from damaging the processor.
Helps reduce the effects of electrical noise
Current
Limiting
Resistor
FROM INPUT
DEVICE
USE TO DROP THE VOLTAGE TO LOGIC LEVEL
Buffer, Filter, hysteresis Circuits
TO
PROCESSOR

## Slide 18
18
I/O Module
AC INPUT MODULE
OPTO-
ISOLATOR
IS NEEDED TO:
Prevent voltage transients from damaging the processor.
Helps reduce the effects of electrical noise
Rectifier,
Resistor
Network
FROM INPUT
DEVICE
CONVERTS THE AC INPUT TO DC AND DROPS THE VOLTAGE TO LOGIC LEVEL
Buffer, Filter, Hysteresis Circuits
TO
PROCESSOR

## Slide 21
21
I/O Module
DC / AC OUTPUT MODULE
OPTO-
ISOLATOR
IS NEEDED TO:
Prevent voltage transients from damaging the processor.
Helps reduce the effects of electrical noise
FROM PROCESSOR
TTL
Circuits
Amplifier
RELAY
TRIAC
X’SISTOR
TO
OUTPUT
DEVICE

## Slide 23
23
I/O Circuits
DIFFERENT TYPES OF I/O CIRCUITS
1. Pilot Duty Outputs
Outputs of this type typically are used to drive high-current electromagnetic loads such as solenoids, relays, valves, and motor starters.
These loads are highly inductive and exhibit a large inrush current.
Pilot duty outputs should be capable of withstanding an inrush current of 10 times the rated load for a short period of time without failure.

## Slide 24
24
I/O Circuits
2. General - Purpose Outputs
These are usually low- voltage and low-current and are used to drive indicating lights and other non-inductive loads. Noise suppression may or may not be included on this types of modules.
3. Discrete Inputs
Circuits of this type are used to sense the status of limit switches, push buttons, and other discrete sensors. Noise suppression is of great importance in preventing false indication of inputs turning on or off because of noise.

## Slide 25
25
I/O Circuits
4. Analog I/O
Circuits of this type sense or drive analog signals.
Analog inputs come from devices, such as thermocouples, strain gages, or pressure sensors, that provide a signal voltage or current that is derived from the process variable.
Standard Analog Input signals: 4-20mA; 0-10V
Analog outputs can be used to drive devices such as voltmeters, X-Y recorders, servomotor drives, and valves through the use of transducers.
Standard Analog Output signals: 4-20mA; 0-5V; 0-10V

## Slide 26
26
I/O Circuits
5. Special - Purpose I/O
Circuits of this type are used to interface PLCs to very specific types of circuits such as servomotors, stepping motors PID (proportional plus integral plus derivative) loops, high-speed pulse counting, resolver and decoder inputs, multiplexed displays, and keyboards.
This module allows for limited access to timer and counter presets and other PLC variables without requiring a program loader.

## Slide 27
Discrete Input
A discrete input also referred as digital input is an input that is either ON or OFF are connected to the PLC digital input. In the ON condition it is referred to as logic 1 or a logic high and in the OFF condition maybe referred to as logic 0 or logic low.
Normally Open Pushbutton
Normally Closed Pushbutton
Normally Open switch
Normally Closed switch
Normally Open contact
Normally closed contact

## Slide 28
IN
PLC
Analog
Input
Module
Tank
Level Transmitter
An analog input is an input signal that has a continuous signal. Typical inputs may vary from 0 to 20mA, 4 to 20mA or 0 to10V.
Below, a level transmitter monitors the level of liquid in the tank. Depending on the level Tx, the signal to the PLC can either increase or decrease as the level increases or decreases.
Analog Input

## Slide 29
OUT
PLC
Digital
Output
Module
Lamp
A discrete output is either in ON or OFF condition.
Solenoids, contactors coils, lamps are example of devices connected to the
Discrete or digital outputs. Below, the lamp can be turned ON or OFF by the PLC output it is connected to.
Digital Output

## Slide 30
OUT
PLC
Analog
Output
Module
An analog output is an output signal that has a continuous signal.
Typical outputs may vary from 0 to 20mA, 4 to 20mA or 0 to10V.
Analog Output
E
P
Pneumatic control valve
Supply air
Electric to pneumatic transducer
0 to 10V

## Slide 31
31
Processor
The processor module contains the PLC’s microprocessor, its supporting circuitry, and its memory system.
The main function of the microprocessor is to analyze data coming from field sensors through input modules, make decisions based on the user’s defined control program and return signal back through output modules to the field devices.
Field sensors: switches, flow, level, pressure, temp. transmitters, etc. Field output devices: motors, valves, solenoids, lamps, or audible devices.
The memory system in the processor module has two parts: a system memory and an application memory.

## Slide 32
32
PLC Operation
Basic Function of a Typical PLC
Read all field input devices via the input interfaces, execute the user program stored in application memory, then, based on whatever control scheme has been programmed by the user, turn the field output devices on or off, or perform whatever control is necessary for the process application.
This process of sequentially reading the inputs, executing the program in memory, and updating the outputs is known as scanning.

## Slide 33
33
While the PLC is running, the scanning process includes the following four phases, which are repeated continuously as individual cycles of operation:
PHASE 2
Program
Execution
PHASE 3
Diagnostics/
Comm
PHASE 4
Output
Scan
PHASE 1
Read Inputs
Scan
PLC Operation

## Slide 34
34
PHASE 1 – Input Status scan
    A PLC scan cycle begins with the CPU reading the status of its inputs.
PHASE 2– Logic Solve/Program Execution
    The application program is executed using the status of the inputs
PHASE 3– Logic Solve/Program Execution
    Once the program is executed, the CPU performs diagnostics and communication tasks
PHASE 4 - Output Status Scan
    An output status scan is then performed, whereby the stored output values are sent to actuators and other field output devices. The cycle ends by updating the outputs.

## Slide 35
35
As soon as Phase 4 are completed, the entire cycle begins again with Phase 1 input scan.
The time it takes to implement a scan cycle is called SCAN TIME. The scan time composed of the program scan time, which is the time required for solving the control program, and the I/O update time, or time required to read inputs and update outputs. The program scan time generally depends on the amount of memory taken by the control program and type of instructions used in the program. The time to make a single scan can vary from 1 ms to 100 ms.

## Slide 36
36
PLC Communications
Common Uses of PLC Communications Ports
Changing resident PLC programs - uploading/downloading from a supervisory controller (Laptop or desktop computer).
Forcing I/O points and memory elements from a remote terminal.
Linking a PLC into a control hierarchy containing several sizes of PLC and computer.
Monitoring data and alarms, etc. via printers or Operator Interface Units (OIUs).

## Slide 37
37
PLC Communications
Serial Communications
PLC communications facilities normally provides serial transmission of information.
Common Standards
RS 232
Used in short-distance computer communications, with the majority of computer hardware and peripherals.
Has a maximum effective distance of approx. 30 m at 9600 baud.

## Slide 38
38
PLC Communications
Local Area Network (LAN)
Local Area Network provides a physical link between all devices plus providing overall data exchange management or protocol, ensuring that each device can “talk” to other machines and understand data received from them.
LANs provide the common, high-speed data communications bus which interconnects any or all devices within the local area.
LANs are commonly used in business applications to allow several users to share costly software packages and peripheral equipment such as printers and hard disk storage.

## Slide 39
39
Specifications
Several factors are used for evaluating the quality and performance of programmable controllers when selecting a unit for a particular application. These are listed below.
NUMBER OF I /O PORTS
This specifies the number of I/O devices that can be connected to the controller. There should be sufficient I/O ports to meet present requirements with enough spares to provide for moderate future expansion.

## Slide 40
Selecting a PLC
    Criteria
    • Number of logical inputs and outputs.
    • Memory
    • Number of special I/O modules
    • Scan Time
    • Communications
    • Software

## Slide 41
A Detailed Design Process
  1. Understand the process
  2. Hardware/software selection
  3. Develop ladder logic
  4. Determine scan times and memory requirements

## Slide 42
42
Specifications
OUTPUT-PORT POWER RATINGS
Each output port should be capable of supplying sufficient voltage and current to drive the output peripheral connected to it.
SCAN TIME
This is the speed at which the controller executes the relay-ladder logic program. This variable is usually specified as the scan time per 1000 logic nodes and typically ranges from 1 to 200 milliseconds.

## Slide 43
43
Specifications
MEMORY CAPACITY
The amount of memory required for a particular application is related to the length of the program and the complexity of the control system. Simple applications having just a few relays do not require significant amount of memory. Program length tend to expand after the system have been used for a while. It is advantageous to a acquire a controller that has more memory than is presently needed.

## Slide 44
PLC Status Indicators
Power On
Run Mode
Programming Mode
Fault

## Slide 45
Troubleshooting
    1. Look at the process
    2. PLC status lights
      HALT - something has stopped the CPU
      RUN - the PLC thinks it is OK (and probably is)
      ERROR - a physical problem has occurred with the PLC
    3. Indicator lights on I/O cards and sensors
    4. Consult the manuals, or use software if available.
    5. Use programming terminal / laptop.

## Slide 46: PLC’s Use Ladder Logic
Ladder Logic Diagrams Provide a Method to Symbolically Show How Relay Control Schemes are Implemented
Relay Contacts and Coils, Inputs and Outputs lie on “Rungs” Between the Positive and Ground Rails

## Slide 47: PLC INSTRUCTIONS
1) Relay,
2) Timer and counter,
3) Program control,
4) Arithmetic,
5) Data manipulation,
6) Data transfer, and
7) Others, such as sequencers.

## Slide 48: RELAY
A Relay consists of two parts, the coil and the contact(s).
Contacts:
a. Normally open -| |-
b. Normally closed -|/|-
c. Off-on transitional -||-
d. On-off transitional -| |-
Coil:
a. Energize Coil -( )-
b. De-energize -(/)-
c. Latch -(L)-
d. Unlatch -(U)-
( )

## Slide 49
PROGRAMMING
Normally Open
(NO)
Normally Closed
(NC)
Power flows through these contacts when they are closed. The
normally open (NO) is true when the input or output status bit
controlling the contact is 1. The normally closed (NC) is true
when the input or output status bit controlling the contact is 0.

## Slide 50
Coils
Coils represent relays that are energized when power flows to them.
When a coil is energized it causes a corresponding output to turn on by changing the state of the status bit controlling
the output to 1.
That same output status bit maybe used to control normally open or normally closed contact anywhere in the program.

## Slide 51: Simple Relay Circuit

## Slide 52: Circuit representation in Ladder Logic
The above circuit is represented in Ladder logic as shown in figure below (only the low voltage circuit is used in ladder logic diagrams):

## Slide 53
Boxes
Boxes represent various instructions or functions that are
Executed when power flows to the box. Some of these
Functions are timers, counters and math operations.

## Slide 54
AND OPERATION
Each rung or network on a ladder program represents
a logic operation. In the rung above, both inputs A and B
must be true (1) in order for the output C to be true (1).
Rung
A
B
C

## Slide 55
OR OPERATION
In the rung above, it can be seen that either input A or B
is be true (1), or both are true, then the output C is true (1).
Rung
A
B
C

## Slide 56
NOT OPERATION
In the rung above, it can be seen that if input A is be true (1),
then the output C is true (0) or when A is (0), output C is 1.
Rung
A
C

## Slide 57: Multi Input/Output Rungs

## Slide 58: TIMERS AND COUNTERS
Timers:
a. Retentive on delay -(RTO)-
b. Retentive off delay -(RTF)-
c. Reset -(RST)-
Counter:
a. Counter up -(CTU)-
b. Counter down -(CTD)-
c. Counter reset -(CTR)-
RTO counting stop counting
resume
RTF stop counting stop
True False True
Input
RTO reach PR value, output ON
RTF reach PR value, output OFF
PR value in 0.1 second

## Slide 59: Programming a PLC
Oil is consumed randomly. The tank needs to be refilled by turning on a pump. Two hydrostatic switches are used to detect a high and low level.

## Slide 60: Ladder Logic for Tank

## Slide 61: Logic for Ladder Solution

## Slide 62: How does it work?

## Slide 64: End of Lecture-5
To download this lecture visit
http://imtiazhussainkalwar.weebly.com/